{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["Sheet1"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":42,"n_cols":11,"rows_kept":42,"merged":[[0,0,0,10],[38,0,38,10],[39,0,39,10]],"flags":["formulas_cached_only"]}
[" 泰州综合管廊材料申购表（2019年度）"]
["锦宸集团有限公司泰州综合管廊工程项目部"]
["序号 ","材料名称","型号及规格","材料","单位","数量","材料采购价（含税价）","材料品牌要求","钢管防腐及颜色要求"," 用途","备注"]
[1,"钢管（满足饮用水卫生要求）","D630*9","Q235","米",2600,null,"天津友发、徐州光环、无锡湖光","钢管防腐要求见备注 钢管外部颜色要求——待定","管廊内给水","钢管长度需扣除管件、阀门所占的长度"]
[2,"钢管（满足饮用水卫生要求）","D530*9","Q235","米",9.56,null,"天津友发、徐州光环、无锡湖光","钢管防腐要求见备注 钢管外部颜色要求——待定","管廊内给水","钢管长度需扣除管件、阀门所占的长度"]
[3,"钢管（满足饮用水卫生要求）","D325*8","Q235","米",158.58,null,"天津友发、徐州光环、无锡湖光","钢管防腐要求见备注 钢管外部颜色要求——待定","管廊内给水","钢管长度需扣除管件、阀门所占的长度"]
[4,"钢管（满足饮用水卫生要求）","D159*6","Q235","米",32.6,null,"天津友发、徐州光环、无锡湖光","钢管防腐要求见备注 钢管外部颜色要求——待定","管廊内给水","钢管长度需扣除管件、阀门所占的长度"]
[5,"钢管固定管卡","50*6","镀锌扁钢","米",1213.03,{"$nulls":3},"管廊内给水","每个条形支墩2个"]
[6,"钢管固定管卡螺母、垫片","M24","Q235","套",1752,{"$nulls":3},"管廊内给水","每个条形支墩4套"]
[7,"手动法兰式伸缩蝶阀","DN600 P=1.0MPa","铸铁","个",21,null,"冠龙、丹麦AVK、德国VAG",null,"管廊内给水"]
[8,"手动法兰式伸缩蝶阀","DN500 P=1.0MPa","铸铁","个",2,null,"冠龙、丹麦AVK、德国VAG",null,"管廊内给水"]
[9,"手动法兰式伸缩蝶阀","DN300 P=1.0MPa","铸铁","个",39,null,"冠龙、丹麦AVK、德国VAG",null,"管廊内给水"]
[10,"手动法兰式伸缩蝶阀","DN150 P=1.0MPa","铸铁","个",11,null,"冠龙、丹麦AVK、德国VAG",null,"管廊内给水"]
[11,"排泥阀（排水阀）","DN200 P=1.0MPa","铸铁","个",9,null,"冠龙、丹麦AVK、德国VAG",null,"管廊内给水"]
[12,"手动法兰式伸缩蝶阀","DN80 P=1.0MPa","铸铁","个",9,null,"冠龙、丹麦AVK、德国VAG",null,"管廊内给水","与透气阀配套使用"]
[13,"透气阀（排气阀）","DN80 P=1.0MPa","铸铁","个",9,null,"冠龙、丹麦AVK、德国VAG",null,"管廊内给水"]
[14,"盲堵","DN600","Q235","个",1,{"$nulls":3},"管廊内给水"]
[15,"法兰盘","DN600","Q235","片",43,{"$nulls":3},"管廊内给水"]
[16,"法兰盘","DN500","Q235","片",4,{"$nulls":3},"管廊内给水"]
[17,"法兰盘","DN300","Q235","片",78,{"$nulls":3},"管廊内给水"]
[18,"法兰盘","DN150 ","Q235","片",22,{"$nulls":3},"管廊内给水"]
[19,"排泥三通","DN600*DN200","Q235","个",9,{"$nulls":3},"管廊内给水"]
[20,"法兰盘","DN200","Q235","片",18,{"$nulls":3},"管廊内给水"]
[21,"法兰盘","DN80","Q235","片",18,{"$nulls":3},"管廊内给水"]
[22,"排气三通","DN600*DN80","Q235","个",9,{"$nulls":3},"管廊内给水"]
[23,"支吊架","50*5角钢","Q235","米",114.3,{"$nulls":3},"管廊内给水","给水分支口固定"]
[24,"支吊架","10#槽钢","Q235","米",17.96,{"$nulls":3},"管廊内给水","给水分支口固定"]
[25,"等径三通","D630*9","Q235","个",1,{"$nulls":3},"管廊内给水","详02S403/48，49"]
[26,"异径三通","D630*D325*8","Q235","个",25,{"$nulls":3},"管廊内给水","详02S403/42，43"]
[27,"异径三通","D630*D530*9","Q235","个",1,{"$nulls":3},"管廊内给水","详02S403/42，43"]
[28,"双盘等径三通","D630*9","Q235","个",1,{"$nulls":3},"管廊内给水","详02S403/48，49"]
[29,"双盘等径三通","D530*9","Q235","个",1,{"$nulls":3},"管廊内给水","详02S403/48，49"]
[30,"双盘等径三通","D325*8","Q235","个",14,{"$nulls":3},"管廊内给水","详02S403/48，49"]
[31,"单盘等径三通","D325*8","Q235","个",11,{"$nulls":3},"管廊内给水","详02S403/48，49"]
[32,"异径管","D325*D159*8","Q235","个",11,{"$nulls":3},"管廊内给水","详02S403/52，53"]
[33,"钢板","150*150*10",null,"块",200,{"$nulls":3},"管廊内接地预埋  "]
[34]
[35]
["备注：1、钢管内防腐：采用液体无毒环氧涂料，产品需具备国家卫生部颁发的饮用水卫生安全的许可证（有效期内），并符合《生活饮用水输配水设备及防护材料的安全评价标准》（GB/T17219-1998),钢管除锈及内防腐，施工和验收严格执（SYT0457-2010)《钢管管道液体环氧涂料内防腐层技术标准》及(GB50268-2008)《给水排水管道工程施工及验收规范》，其中干膜厚度不小于200um,两道底漆，两道面漆。                                                                                           2、管廊内钢管外防腐：采用涂料防腐，具体做法为环氧富锌底漆两遍，不小于80um；环氧云铁中间漆一遍，不小于60um；丙烯酸防腐磁漆两遍，不小于80um；总厚度不小于220um。                                                                                                                                         3、单、双盘等径三通均不含两侧法兰盘，如果购买成品等径三通两侧带法兰盘，材料表中需减去相对应法兰盘的数量。"]
["审核：                  预算：                   现场：                  申报："]
[]
["                                                                            日期：   年    月    日"]