{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["Sheet1"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":19,"n_cols":11,"rows_kept":19,"merged":[[0,0,0,10],[15,0,15,10],[16,0,16,10]],"flags":["formulas_cached_only"]}
[" 泰州综合管廊材料申购表（2019年度）"]
["锦宸集团有限公司泰州综合管廊工程项目部"]
["序号 ","材料名称","型号及规格","材料","单位","数量","材料采购单价（含税价）","材料采购合价（含税价）","材料品牌要求"," 用途","备注"]
[1,"室外地上式消火栓","（SS150/80-1.0Mpa)"," ","套",54,{"$nulls":3},"管廊外消火栓与给水管道连接","图集号01S201-13"]
[2,"蝶阀 "," DN150    D71X-10"," ","个",54,null,null,"冠龙、丹麦AVK、德国VAG","管廊外消火栓与给水管道连接"]
[3,"钢管","D159*6","Q235","米",337.5,null,null,"天津友发、徐州光环、无锡湖光","管廊外消火栓与给水管道连接","钢管长度需扣除管件、阀门所占的长度"]
[4,"90°弯头","DN150","Q235","个",216,{"$nulls":3},"管廊外消火栓与给水管道连接"]
[5,"法兰盘","DN150 ","Q235","片",162,{"$nulls":3},"管廊外消火栓与给水管道连接"]
[6,"异径三通","D630*159","Q235","个",2,{"$nulls":3},"管廊外消火栓与给水管道连接"]
[7,"异径三通","D530*159","Q235","个",2,{"$nulls":3},"管廊外消火栓与给水管道连接"]
[8,"异径三通","D325*159","Q235","个",39,{"$nulls":3},"管廊外消火栓与给水管道连接"]
[9,"等径三通"," D159","Q235","个",11,{"$nulls":3},"管廊外消火栓与给水管道连接"]
[10,"橡胶垫片","DN150 ","橡胶","片",162,{"$nulls":3},"管廊外消火栓与给水管道连接"]
[11]
[12]
["备注：1、钢管内防腐：采用液体无毒环氧涂料，产品需具备国家卫生部颁发的饮用水卫生安全的许可证（有效期内），并符合《生活饮用水输配水设备及防护材料的安全评价标准》（GB/T17219-1998),钢管除锈及内防腐，施工和验收严格执（SYT0457-2010)《钢管管道液体环氧涂料内防腐层技术标准》及(GB50268-2008)《给水排水管道工程施工及验收规范》，其中干膜厚度不小于200um,两道底漆，两道面漆。                                                                                           2、管廊内钢管外防腐：采用涂料防腐，具体做法为环氧富锌底漆两遍，不小于80um；环氧云铁中间漆一遍，不小于60um；丙烯酸防腐磁漆两遍，不小于80um；总厚度不小于220um。                                                                                                                                         "]
["审核：                  预算：                   现场：                  申报："]
[]
["                                                                            日期：   年    月    日"]